## HL_E
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | High Load Existing | 1a | -25 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 0 | 1g | -23 | 30 | 0.5 | 31.5 | -45
Cross Section Tag | hl | 1b | -20 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 120 | 2g | 3 | 30 | 0.5 | 0 | -45
Subtitle | test | 1c | -15 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 240 | 3g | 17 | 30 | 0.5 |  | 45
Frequency (Hertz) | 60 | 2a | -5 | 24 | 1 | 0.97 | 0.97 | 315 | 1355 | 0 | [5 empty] | 45
Soil Resistivity (Ohm-meter) | 100 | 2b | 0 | 24 | 1 | 0.97 | 0.97 | 315 | 1355 | 120
Max Horizontal Distance From Reference (ft) | 100 | 2c | 5 | 24 | 1 | 0.97 | 0.97 | 315 | 1355 | 240
Step Size (ft) | 1 | 3a | 15 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 0
Height For Field Calculation (ft) | 3 | 3b | 20 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 120
Left Coordinate of Right of Way (ft) | -45 | 3c | 25 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 240
Right Coordinate of Right of Way (ft) | 45
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## HL_P
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | High Load Proposed | 1a | -25 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 0 | 1g | -23 | 30 | 0.5 | 37.8 | -45
Cross Section Tag | hl | 1b | -20 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 120 | 2g | 3 | 30 | 0.5 | 0 | -45
Subtitle | test | 1c | -15 | 24 | 1 | 0.97 | 0.97 | 345 | 1664 | 240 | 3g | 17 | 36 | 0.5 |  | 45
Frequency (Hertz) | 60 | 2a | -5 | 24 | 1 | 0.97 | 0.97 | 315 | 1355 | 0 | [5 empty] | 45
Soil Resistivity (Ohm-meter) | 100 | 2b | 0 | 24 | 1 | 0.97 | 0.97 | 315 | 1355 | 120
Max Horizontal Distance From Reference (ft) | 100 | 2c | 5 | 24 | 1 | 0.97 | 0.97 | 315 | 1355 | 240
Step Size (ft) | 1 | 3a | 17 | 22 | 1 | 0.97 | 0.97 | 345 | 1664 | 0
Height For Field Calculation (ft) | 3 | 3b | 23 | 27 | 1 | 0.97 | 0.97 | 345 | 1664 | 120
Left Coordinate of Right of Way (ft) | -45 | 3c | 17 | 32 | 1 | 0.97 | 0.97 | 345 | 1664 | 240
Right Coordinate of Right of Way (ft) | 45
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## und_E
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Underground Existing | 3b | -8.42 | 44.17 | 1 | 1.29 | 1.29 | 1150 | 1664 | 120 | 3g | -6.33 | 55.17 | 1 | 57.9285 | -50
Cross Section Tag | und | 3c | -11.67 | 32.17 | 1 | 1.29 | 1.29 | 1150 | 1664 | 240 | 1g | 4.33 | 55.17 | 1 | 0 | -50
Subtitle | Post-Project, Mile 7.65 to Mile 7.88 | 3a | -8.75 | 20.17 | 1 | 1.29 | 1.29 | 1150 | 1664 | 0 | ng | 23 | 36 | 1 |  | 50
Frequency (Hertz) | 60 | 1c | 6.42 | 44.17 | 1 | 1.29 | 1.29 | 1150 | 1664 | 240 | [5 empty] | 50
Soil Resistivity (Ohm-meter) | 100 | 1a | 9.67 | 32.17 | 1 | 1.29 | 1.29 | 1150 | 1664 | 0
Max Horizontal Distance From Reference (ft) | 150 | 1b | 6.75 | 20.17 | 1 | 1.29 | 1.29 | 1150 | 1664 | 120
Step Size (ft) | 1 | nc | 15 | 33 | 1 | 0.68 | 0.68 | 3450 | 764 | 240
Height For Field Calculation (ft) | 3 | nb | 20 | 33 | 1 | 0.68 | 0.68 | 3450 | 764 | 120
Left Coordinate of Right of Way (ft) | -50 | na | 25 | 33 | 1 | 0.68 | 0.68 | 3450 | 764 | 0
Right Coordinate of Right of Way (ft) | 50
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## und_P
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Underground Proposed | 3b | -8.42 | 44.17 | 1 | 1.29 | 1.29 | 115 | 330 | 120 | 3g | -6.33 | 55.17 | 1 | 57.9285 | -50
Cross Section Tag | und | 3c | -11.67 | 32.17 | 1 | 1.29 | 1.29 | 115 | 330 | 240 | 1g | 4.33 | 55.17 | 1 | 0 | -50
Subtitle | Post-Project, Mile 7.65 to Mile 7.88 | 3a | -8.75 | 20.17 | 1 | 1.29 | 1.29 | 115 | 330 | 0 | [5 empty] | 50
Frequency (Hertz) | 60 | 1c | 6.42 | 44.17 | 1 | 1.29 | 1.29 | 115 | 330 | 240 | [5 empty] | 50
Soil Resistivity (Ohm-meter) | 100 | 1a | 9.67 | 32.17 | 1 | 1.29 | 1.29 | 115 | 330 | 0
Max Horizontal Distance From Reference (ft) | 150 | 1b | 6.75 | 20.17 | 1 | 1.29 | 1.29 | 115 | 330 | 120
Step Size (ft) | 1 | nc | 18.67 | -5 | 1 | 0.68 | 0.68 | 345 | 450 | 240
Height For Field Calculation (ft) | 3 | nb | 19 | -5 | 1 | 0.68 | 0.68 | 345 | 450 | 120
Left Coordinate of Right of Way (ft) | -50 | na | 19.33 | -5 | 1 | 0.68 | 0.68 | 345 | 450 | 0
Right Coordinate of Right of Way (ft) | 50
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## 14E
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Section 14 Existing | nc | -24.5 | 21 | 1 | 0.68 | 0.68 | 34.5 | 37 | 240 | 3g | -11 | 52.66 | 1 | 55.293 | -24.5
Cross Section Tag | 14 | nb | -19.5 | 22 | 1 | 0.68 | 0.68 | 34.5 | 37 | 120 | 1g | -8 | 52.66 | 1 | 0 | -24.5
Subtitle | test | na | -14.5 | 21 | 1 | 0.68 | 0.68 | 34.5 | 37 | 0 | [5 empty] | 24.5
Frequency (Hertz) | 60 | 3b | -18.5 | 45.08 | 1 | 0.52 | 0.52 | 115 | 301 | 120 | [5 empty] | 24.5
Soil Resistivity (Ohm-meter) | 100 | 3c | -21.5 | 35.5 | 1 | 0.52 | 0.52 | 115 | 301 | 240
Max Horizontal Distance From Reference (ft) | 50 | 3a | -18.5 | 27.5 | 1 | 0.52 | 0.52 | 115 | 301 | 0
Step Size (ft) | 1 | 1c | -0.5 | 45.08 | 1 | 0.52 | 0.52 | 115 | 316 | 240
Height For Field Calculation (ft) | 3 | 1a | 2.5 | 35.5 | 1 | 0.52 | 0.52 | 115 | 316 | 0
Left Coordinate of Right of Way (ft) | -24.5 | 1b | -0.5 | 27.5 | 1 | 0.52 | 0.52 | 115 | 316 | 120
Right Coordinate of Right of Way (ft) | 24.5
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## 14P
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Section 14 Proposed | 3b | -33.42 | 55 | 1 | 1.29 | 1.29 | 115 | 301 | 120 | 3g | -27.5 | 69.25 | 1 | 72.7125 | -24.5
Cross Section Tag | 14 | 3c | -36.67 | 43 | 1 | 1.29 | 1.29 | 115 | 301 | 240 | 1g | -24.5 | 69.25 | 1 | 0 | -24.5
Subtitle | test | 3a | -33.75 | 31 | 1 | 1.29 | 1.29 | 115 | 301 | 0 | [5 empty] | 24.5
Frequency (Hertz) | 60 | 1c | -18.58 | 55 | 1 | 1.29 | 1.29 | 115 | 316 | 240 | [5 empty] | 24.5
Soil Resistivity (Ohm-meter) | 100 | 1a | -15.33 | 43 | 1 | 1.29 | 1.29 | 115 | 316 | 0
Max Horizontal Distance From Reference (ft) | 50 | 1b | -18.25 | 31 | 1 | 1.29 | 1.29 | 115 | 316 | 120
Step Size (ft) | 1 | nc | -11.33 | -5 | 1 | 0.68 | 0.68 | 34.5 | 37 | 240
Height For Field Calculation (ft) | 3 | nb | -11 | -5 | 1 | 0.68 | 0.68 | 34.5 | 37 | 120
Left Coordinate of Right of Way (ft) | -24.5 | na | -10.67 | -5 | 1 | 0.68 | 0.68 | 34.5 | 37 | 0
Right Coordinate of Right of Way (ft) | 24.5
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## 18E
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Section 18 Existing | 3c | -37.5 | 33 | 1 | 0.52 | 0.52 | 115 | 301 | 240 | 3g | -31.25 | 47.5 | 1 | 49.875 | -60
Cross Section Tag | 18 | 3a | -25 | 33 | 1 | 0.52 | 0.52 | 115 | 301 | 0 | 3h | -18.75 | 47.5 | 1 | 0 | -60
Subtitle | test | 3b | -12.5 | 33 | 1 | 0.52 | 0.52 | 115 | 301 | 120 | 1g | 30.75 | 40.75 | 1 |  | 60
Frequency (Hertz) | 60 | 1b | 13.5 | 25 | 1 | 0.52 | 0.52 | 115 | 316 | 120 | [5 empty] | 60
Soil Resistivity (Ohm-meter) | 100 | 1c | 25 | 25 | 1 | 0.52 | 0.52 | 115 | 316 | 240
Max Horizontal Distance From Reference (ft) | 100 | 1a | 36.5 | 25 | 1 | 0.52 | 0.52 | 115 | 316 | 0
Step Size (ft) | 1
Height For Field Calculation (ft) | 3
Left Coordinate of Right of Way (ft) | -60
Right Coordinate of Right of Way (ft) | 60
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## 18P
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Section 18 Proposed | 3c | -32.5833 | 28.5 | 1 | 1.293 | 1.293 | 115 | 301 | 240 | 3g | -25 | 54.83 | 1 | 57.5715 | -60
Cross Section Tag | 18 | 3a | -17.4167 | 34.5 | 1 | 1.293 | 1.293 | 115 | 301 | 0 | 1g | 25 | 54.83 | 1 | 0 | -60
Subtitle | test | 3b | -32.5833 | 40.5 | 1 | 1.293 | 1.293 | 115 | 301 | 120 | [5 empty] | 60
Frequency (Hertz) | 60 | 1b | 17.4167 | 28.5 | 1 | 1.293 | 1.293 | 115 | 316 | 120 | [5 empty] | 60
Soil Resistivity (Ohm-meter) | 100 | 1c | 32.58 | 34.5 | 1 | 1.293 | 1.293 | 115 | 316 | 240
Max Horizontal Distance From Reference (ft) | 100 | 1a | 17.4167 | 40.5 | 1 | 1.293 | 1.293 | 115 | 316 | 0
Step Size (ft) | 1
Height For Field Calculation (ft) | 3
Left Coordinate of Right of Way (ft) | -60
Right Coordinate of Right of Way (ft) | 60
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it.

## 32E
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Section 32 Existing | 1c | -234.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 240 | 1g | -222 | 46.66 | 1 | 97.909 | -150
Cross Section Tag | 32 | 1b | -200 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 120 | 1h | -178 | 46.66 | 1 | 0 | -150
Subtitle | test | 1a | -165.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 0 | 2g | -72 | 46.66 | 1 |  | 150
Frequency (Hertz) | 60 | 2c | -84.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 240 | 2h | -28 | 46.66 | 1 |  | 150
Soil Resistivity (Ohm-meter) | 100 | 2b | -50 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 120 | tg | 136 | 93.2467 | 1
Max Horizontal Distance From Reference (ft) | 300 | 2a | -15.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 0 | 5g | 164 | 88.5867 | 1
Step Size (ft) | 1 | ta | 129 | 22.33 | 1 | 1.735 | 1.735 | 345 | 2468 | 0
Height For Field Calculation (ft) | 3 | tb | 124 | 45.33 | 1 | 1.735 | 1.735 | 345 | 2468 | 120
Left Coordinate of Right of Way (ft) | -150 | tc | 128 | 68.33 | 1 | 1.735 | 1.735 | 345 | 2468 | 240
Right Coordinate of Right of Way (ft) | 150 | 5c | 171 | 17.67 | 1 | 1.735 | 1.735 | 115 | 2468 | 240
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it. |  | 5b | 176 | 40.67 | 1 | 1.735 | 1.735 | 115 | 2468 | 120
|  | 5a | 172 | 63.67 | 1 | 1.735 | 1.735 | 115 | 2468 | 0

## 32P
FIELDS Template
Title, Plotting, and Miscellaneous Inputs |  | Phase Conductor Descriptions | [8 empty] | Ground Wire Descriptions |  |  |  | ROW Edge Lines - IGNORE THIS
Input Name | Input Value | Hot Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Subconductors per Bundle | Conductor Diameter (in) | Bundle Diameter (in) | Phase-Phase (kV) | Phase Current (Amp) | Phase Angle (deg) | Ground Wire Tag | Horizontal Coordinate (ft) | Height (ft) | Diameter (in) | Y - max vertical coordinate + 5 % | X - ROW edges
Main Title | Section 32 Proposed | 1c | -234.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 240 | 1g | -222 | 46.66 | 1 | 97.909 | -275
Cross Section Tag | 32 | 1b | -200 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 120 | 1h | -178 | 46.66 | 1 | 0 | -275
Subtitle | test | 1a | -165.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 0 | 2g | -72 | 46.66 | 1 |  | 275
Frequency (Hertz) | 60 | 2c | -84.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 240 | 2h | -28 | 46.66 | 1 |  | 275
Soil Resistivity (Ohm-meter) | 100 | 2b | -50 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 120 | tg | 136 | 93.2467 | 1
Max Horizontal Distance From Reference (ft) | 300 | 2a | -15.5 | 22.33 | 1 | 1.04 | 1.04 | 345 | 2694 | 0 | 5g | 164 | 88.5867 | 1
Step Size (ft) | 1 | ta | 129 | 22.33 | 1 | 1.735 | 1.735 | 345 | 2468 | 0 | 3g | 219.6667 | 58.42 | 1
Height For Field Calculation (ft) | 3 | tb | 124 | 45.33 | 1 | 1.735 | 1.735 | 345 | 2468 | 120 | 0g | 230.3333 | 58.42 | 1
Left Coordinate of Right of Way (ft) | -275 | tc | 128 | 68.33 | 1 | 1.735 | 1.735 | 345 | 2468 | 240
Right Coordinate of Right of Way (ft) | 275 | 5c | 171 | 17.67 | 1 | 1.735 | 1.735 | 115 | 2468 | 240
Do any scratch calculations or miscellaneous copying/pasting below here, in this section. Scripts will ignore it. |  | 5b | 176 | 40.67 | 1 | 1.735 | 1.735 | 115 | 2468 | 120
|  | 5a | 172 | 63.67 | 1 | 1.735 | 1.735 | 115 | 2468 | 0
|  | 3c | 217.5833 | 20.17 | 1 | 1.29 | 1.29 | 115 | 1664 | 0
|  | 3a | 214.3333 | 32.17 | 1 | 1.29 | 1.29 | 115 | 1664 | 240
|  | 3b | 217.25 | 44.17 | 1 | 1.29 | 1.29 | 115 | 1664 | 120
|  | 0b | 232.4167 | 20.17 | 1 | 1.29 | 1.29 | 115 | 1664 | 120
|  | 0c | 235.6667 | 32.17 | 1 | 1.29 | 1.29 | 115 | 1664 | 0
|  | 0a | 232.75 | 44.17 | 1 | 1.29 | 1.29 | 115 | 1664 | 240